## Intro
f-EASY (SDH)
Simple calculator for quick feasibility study of solar district heating
J.E.Nielsen, PlanEnergi |  | version 0.8 | 21/9 2012
Introduction
This calculator gives an quick estimate of the economy of the solar part of a solar district heating system
This sheet "Intro" gives an introduction to how to use the calculator
In the sheet "Calculator" the calculations can be done
The calculator needs at minimum 7 input - see "Main inputs".
16 + 2 more specific/detailed inputs can be given - see "Detailed inputs" and "Main results"
When the value in the left column "Own or calc" = "Calc", then the "Value used" is calculated according to [1]
When the value in the left column "Own or calc" = "Calc", then the value given in "Own input" is ignored
When the value in the left column "Own or calc" = "Own", then the "Value used" = "Own value"
[1] SDH Fact sheet 2.3 Feasilibility study - download from: | http://www.solar-district-heating.eu/Factsheets
The sole responsibility for the content of this publication lies with the authors. However neither the authors nor EACI, nor the European Commission is responsible for any use that may be made of the information contained therein. It does not necessarily reflect the opinion of the European Union.

## Calculator
f-EASY (SDH)
Simple calculator for quick feasibility study of solar district heating
J.E.Nielsen, PlanEnergi |  |  | version 0.8 | 21/9 2012
Main inputs
Own or Calc | Parameter | Own input | Value used | Unit | Name | Formula | Regression constants | [5 empty] | Calc
Own | Total load on network (= annual production) | 20000 | 20000 | MWh | Prod | [5 empty] | Own
Calc
Own | Solar irradiation on horizontal at location | 1000 | 1000 | kWh/m² | G0
Own | Land area available | 30000 | 30000 | m² | Aland
Own | Price per m² land | 5 | 5 | €/m² | Pland
Own | Distance to network connection | 0.5 | 0.5 | km | Dloc
Own | Average operating temperature - network side | 60 | 60 | °C | Top
Own | Acceptable heat production price | 60 | 60 | €/MWh | Pheat
Main results
Own or Calc | Parameter | Own input | Value used | Unit | Name | Formula | Regression constants
Calc | Collector area | 0 | 10000 | m² | Ac | min(Aland/3;Prod/0.5)
Calc | Land area used | 0 | 30000 | m² | Alanduse | Ac*3
Calc | Storage volume | 0 | 3575.5819 | m3 | Vs | Vs_Ac*Ac
Calc | Total investment |  | 3.8137 | Mio € | Itot | Pm+Pdo+Subtot
Calc | Simpel payback time |  | 16.1692 | Years | SPT
Detailed inputs
Own or Calc | Parameter | Own input | Value used | Unit | Name
Calc | Land costs | 0 | 0.15 | mio € | Ptotland | Alanduse*Pland/1000000
Calc | Transmission heat losses | 0 | 0.564 | % | Qtrans | Dloc*(100/Ac + 0.128/SQRT(Ac))
Calc | Costs of transmission piping | 0 | 0.13 | mio € | Ptottrans | 2600 * SQRT(Ac) | cpc0+cpc1_*Ac+cpc2_*Ac^2
[7 empty] | cpc0 | cpc1 | cpc2
Calc | Costs of collector field per m² (incl. installation) | 0 | 242.6747 | €/m² | pc | cpc0+cpc1_*Ac+cpc2_*Ac^2 | 299.44 | -0.0041 | 3.8e-08 | -323 | 4795
Calc | Costs of collector field (incl. installation) | 0 | 2.4267 | mio € | Ptotc | pc*Ac/1000000
cQsol
Calc | Nominal solar output (Top = 50°C) | 0 | 5000 | MWh | Qsol0 | cQsol*G0*Ac/1000 | 0.5
[7 empty] | cRT0 | cRT1 | cRT2
Calc | Solar output - temperature corrected | 0 | 4273 | MWh | Qsol1 | (cRT0+cRT1_*Top+cRT2_*Top^2)*Qsol0 | 2 | -0.0244 | 8.85e-05
Calc | Solar output - corrected for transmissions losses | 0 | 4248.9003 | MWh | Qsol2 | Qsol1-Qtrans
Calc | Solar fraction |  | 21.24% | - | SF | Qsol2/Prod
cV0
Calc | Storage volume per collector area | 0 | 0.35756 | m3/m2 | Vs_Ac | hvis(SF<0.2;0;SF*cV0)
[11 empty] | cx0 | cx1 | px
Calc | Store type | None | Steel tank | - | S_type | IF(C57=S57;HVIS(Vs<=10000;S59;"Pond/Borehole");C57)) |  |  |  | Calc
None
Calc | Storage cost all included | 0 | 0.60955 | mio € | Ps | IF(H57="Steel tank";px_steel;px_pond))/1000000 |  |  |  | Steel tank | 134000 | 133 | 609552.3924
[10 empty] | Pond/Borehole | 650000 | 20 | 721511.638
Calc | Other costs - ground levelling | 0 | 0 | Mio € | Pgl | 0
Calc | Other costs - buildings | 0 | 0 | Mio € | Pb | 0
Calc | Subtotal |  | 3.3163 | Mio € | Subtot | Pb+Pgl+Ps+Ptotc+Ptotland+Ptottrans
cPdo
Calc | Other costs - design and optimization | 0 | 0.16581 | Mio € | Pdo | Subtot*cPdo | 0.05
cPm
Calc | Other costs - misc. | 0 | 0.33163 | Mio € | Pm | Subtot*cPm | 0.1
cPop
Calc | Operational costs - annually | 0 | 0.019069 | Mio € | Pop | Itot*cPop | 0.005

## temp (hidden)
2
-0.0244
8.85e-05
| I | II |  | Collector I | Collector II | ave
30 | 546 | 563 | 30 | 142.6% | 127.1% | 134.8% | 1.3476
40 | 460 | 500 | 40 | 120.1% | 112.9% | 116.5% | 1.1656
50 | 383 | 443 | 50 | 100% | 100% | 100% | 1.0012
60 | 315 | 393 | 60 | 82.25% | 88.71% | 85.48% | 0.8546
70 | 255 | 348 | 70 | 66.58% | 78.56% | 72.57% | 0.72565
80 | 204 | 307 | 80 | 53.26% | 69.3% | 61.28% | 0.6144
[8 empty] | Average operating temperature - network side | 60 | °C
Relative solar output

## SF (hidden)
Solar Output versus Solar Fraction
|  | 1 | 1 | 1
|  | -0.001 | -0.0015 | -0.002
|  | -2e-05 | -3e-05 | -4e-05
|  | A = 100 000 m² | A = 10 000 m² | A = 1 000 m²
| 0 | 1 | 1 | 1
| 10 | 0.988 | 0.982 | 0.976
| 20 | 0.972 | 0.958 | 0.944
| 30 | 0.952 | 0.928 | 0.904
| 40 | 0.928 | 0.892 | 0.856
| 50 | 0.9 | 0.85 | 0.8
| 60 | 0.868 | 0.802 | 0.736
| 70 | 0.832 | 0.748 | 0.664
| 80 | 0.792 | 0.688 | 0.584
| 90 | 0.748 | 0.622 | 0.496
| 100 | 0.7 | 0.55 | 0.4

## Field costs (hidden)
299.44
|  | 1.2 | 0.2 |  | -0.0041
3.8e-08
2000 | 1821 | 291.36 | 233.088 | 349.632 | 291.392
12500 | 1590.8486 | 254.5358 | 203.6286 | 305.4429 | 254.1275
25000 | 1375 | 220 | 176 | 264 | 220.69
37500 | 1250 | 200 | 160 | 240 | 199.1275
50000 | 1183.3333 | 189.3333 | 151.4667 | 227.2 | 189.44

## storage (hidden)
Store volume |  |  | €/kr | 7.5
| SF | V/A |  | V in m3 | 2000 | 10000 | 50000 | 100000
| 0 | 0 |  | Steel tank | 1500 | 1000 |  |  | kr/m3
| 1 | 4 |  | Pond |  |  | 250 | 150 | kr/m3
|  |  |  | Borehole |  |  | 250 | 150 | kr/m3
|  |  |  | V in m3 | 2000 | 10000 | 50000 | 100000
|  |  |  | Steel tank | 200 | 133.3333 |  |  | €/m3
|  |  |  | Pond |  |  | 33.3333 | 20 | €/m3
|  |  |  | Borehole |  |  | 33.3333 | 20 | €/m3
|  |  |  | Volume | Steel tank | Pond / Borehole
|  |  |  | 2000 | 400000 |  | 200
|  |  |  | 10000 | 1464000 |  | 133
|  |  |  | 50000 |  | 1650000 | 33
|  |  |  | 100000 |  | 2650000 | 20
650000
20